## Sheet1
DLF TOWERS FIRE & SAFTY APPROVAL FORMAT
SHOP / UNIT NUMBER ____________________TOWER___________________
Review Requested on ____________________
Review Done on _________________________
TYPE OF INSPECTION : Fire and safety check
SR.NO. | Description | Status | Remarks
FIRE AND SAFETY
Fire Norms to be followed by the tenant
Sprinkler System – Important compliance
1 | Only fast response sprinkler are permitted.
2 | Check fire adequacy of the pipe line as per size and number of sprinkler as mentioned.
25 NB: 2 Sprinkler
32 NB: 3 Sprinkler
40 NB: 6 Sprinkler
50 NB: 18 Sprinkler
3 | Only right pipe supports permitted.
4 | No valve are permitted in fire pipe line.
5 | Ensure that check water line and drain are clear of the sprinkler network.
6 | No welding permitted for up to 50mm dia pipes.
7 | In F&B units – Pantry raised sprinkler are to be planned the kitchen area.
Sprinkler System – Check list for drawings submitted by the tenant .
1 | Sprinkler system above false ceiling has been provided by DLF. | Yes
2 | Check if the sprinkler network for the space below false ceiling is being provided. | Yes/No
3 | Max. distance is 3m dia of line sprinkler -full shop in sprinkler coverage. | Yes/No
4 | Additional sprinklers are planned and drops done for added partitions and cabins. | Yes/No
5 | False ceiling being provided by tenant. | Yes/No
Smoke detector system-Important compliances
1 | Response indicator locations marked on drawing located outside shop: must be connected to the detector system
2 | Ensure that wiring is completely as per the instruction of the fire officer for below false ceiling detectors. The locations planned and numbers as per the minimum coverage norms.
3 | Shops of 1000 sft and below specific area- no detectors required above the false ceiling as sprinkler system will take care of the detection and suppression of any fire.
4 | All cubicles and partions to be counted as "separate spaces" for fire coverage requiring their own sprinkler and smoke detector unless they are 800 mm clear and open below the false ceiling.
5 | Smoke detector required above the false ceiling only if the clear height between fire RCC step & fire flash ceiling exceeds 800 mm.
Smoke detector system- check first for drawing submitted by the tenant.
1 | Smoke detector system drawing submitted. | Yes/No
2 | Smoke dector system drawing complaint as per fire codes- ie coverage area approx 500 sqf per detector. | Yes/No
| Accesses to all smojke detector to be provided for maintainace purpose-paln to be show accesse point. | Yes/No
| In F & B units - heat detector and pentry rated sprinkler are planned for kitchen area. | Yes/No
Electricals -Importaint compliance
1 | Tenant to ensure that one circuit is used for not more than 8 points or 2 power points.
2 | Tenant to ensure that no pvc conduites are used, only MS conduites are to be used and flexible GI pipes required.
3 | Location of main incomer should be in accessible position - in acse of emergency should be easy to put off easily.
4 | Energy efficient light to be used by the electronic choke lights.
HVAC- Importaint compliances
1 | Check for the avaliabilty of VCD between AHU and duct.
Other importaint compliances
1 | Exit signage- to be placed inside the unit pointing outwards from the main shop door and the emergency exit door.
2 | Emergency light to be provided by the tenant in the unit.
3 | Fire exitinguishers, to be placed closed to the main electrical distribution board of the unit on line wall.These can be recessed but must remain easily accebbile.
4 | Before start of interior works the tenant to ensure fire extinguisher, sand buckets and water buckets are palced at different location on each floor of the premises when the tenant is starting the interiors.
5 | The tenant to refrain from use of cooking gas in their pentries public kitchens.
6 | No gas cylender are permitted for any purpose at site.
Additional checks for F & B outlets
1 | Drawings submitted showing the routes and the installation of scrubbers and air washers. | Yes/No
2 | Installation of emergency ventilation system for the kitchen area and the dining area drawing attached. | Yes/No
Please note: All the work will be as per guide line above.
| Acrhitect | Shop Owner

## Sheet2
CERTIFICATE FOR FIRE SAFETY EQUIPMENTS & INSTALLTIONS PROVIDED IN OFFICES/
SHOP NO. IN DLF CORPORATE GREENS' TOWERS, SEC.-74A GURGAON.
1. It is here by certified that while doing the interior fit outs / works,the fire
safety lay out and fire safety equipments/installation which were providede
by DLF with in pramises of Office/Shops No./No's__________ , and the common
area of this said building have npot been chanded in any manners what so ever.
2. Further, while excuting the interiors additional fire safety equipments/installation
code/regulations under national building code 2005 and the same are fully operational
and intigrated with the Buildingh Service System.
3. All wood work has been given to coat's of the retardent paint and all other material used
are of one hours fire rating.
FOR__________________________
Sd/-
Authorised Fire Consultant

## Sheet3
CERTIFICATE FOR FIRE SAFETY EQUIPMENTS & INSTALLTIONS PROVIDED IN OFFICES/SHOP NO. IN DLF CORPORATE GREENS' TOWERS, SEC.-74A GURGAON.
1. It is here by certified that while doing the interior fit outs / works, the fire safety lay out and fire safety equipments/installation which were provided by DLF with in premises of Office/Shops No./No's__________ , and the common area of this said building have not been changed in any manners what so ever.
2. Further, while executing the interiors additional fire safety equipments/installation code/regulations under national building code 2005 and the same are fully operational and integrated with the Building Service System.
3. All wood work has been given to coats of the retardant paint and all other material used are of one hours fire rating.
FOR__________________________
Sd/-
Authorised Fire Consultant